## T2O
EPC100E:I.Data[n] |  |  |  | Integers | [5 empty] | Size: | 108
n | Value | EPC-100E Register | Bits: | Bits 1 | Bits 2 | Bits 3 | Bits 4 | Bits 5 | Bits 6 | Data Type: | INT
0 | Left Exh TC Temp | 30001 | 0 | Left Bank Stepper Rich Limit | Left Bank Step Coil Open Pin F | Right Getting Leaner | Dual Bank System | Calc Flex CSD Hi/Lo | Output B Auto Operation Active | Instance: | 100
1 | Right Exh TC Temp | 30002 | 1 | Left Bank Stepper Lean Limit | Left Bank Step Coil Open Pin A | Right Very Lean Offset | Single Bank System | Cat Temp Delta I/O Lo CSD | Output C, Logic1 is On, No CSD
2 | Left Exh O2 Volt | 30003 | 2 | Left Bank O2 Sensor Not Ready | Left Bank Step Coil Open Pin B | Right Lean | Reserved | Cat Temp Delta I/O Hi CSD | Output A Catalyst Alarm
3 | Right Exh O2 Volt | 30004 | 3 | Left Aux Auto Inhibit | Left Bank Step Coil Open Pin C | Right on Target | Reserved | Cat Temp Out Lo CSD | Output A, Logic1 is On, Running
4 | Left Stepper Position | 30005 | 4 | Left Bank O2 Signal High | Right Bank Step Coil Open Pin F | Right Rich | Reserved | Cat Temp Out Hi CSD | Output Alarm Legacy ALM+PSD
5 | Right Stepper Position | 30006 | 5 | Left Bank O2 Signal Low | Right Bank Step Coil Open Pin A | Right Very Rich Offset | Reserved | Cat Temp In Lo CSD | No Function
6 | Cold Junction Temperature | 30007 | 6 | Left Bank Exh Temp High | Right Bank Step Coil Open Pin B | Right Getting Richer | Right Stepper Power On | Cat Temp in Hi CSD | No Function
7 | Supply Voltage *10 | 30008 | 7 | Left Bank Exh Temp Low | Right Bank Step Coil Open Pin C | Right Auto Control is Active | Left Stepper Power On | Exh Temp Delta Hi L/R CSD | No Function
8 | Logic Voltage (mV) | 30009 | 8 | Unacknowledged Alarm Present | Right Bank Stepper Rich Limit | Left Getting Leaner | Left Bank Step Coil 4 On | Calc Flex PSD Hi/Lo | Cat Out O2 Lo CSD
9 | Left Est. LAMBDA | 30010 | 9 | Reserved | Right Bank Stepper Lean Limit | Left Very Lean Offset | Left Bank Step Coil 3 On | Cat Temp I/O Delta Lo PSD | Left Bank Step Coil 3 On
10 | Right Est. LAMBDA | 30011 | 10 | Right Bank Setepper Resetting | Right Bank O2 Sensor Not Ready | Left Lean | Left Bank Step Coil 2 On | TC Cat Delta Hi Delta PSD | Cat In O2 Lo CSD
11 | Catalyst In TC | 30012 | 11 | Left Bank Stepper Resetting | Right Aux Auto Inhibit | Left on Target | Left Bank Step Coil 1 On | TC Cat Out Hi Temp PSD | Left Bank Step Coil 1 On
12 | Catalyst Out TC | 30013 | 12 | Right Bank Warm-up | Right Bank O2 Signal High | Left Rich | Right Bank Step Coil 4 On | TC Cat In Hi Temp PSD | Right Eng O2 Lo CSD
13 | Left AUX O2 | 30014 | 13 | Left Bank Warm-up | Right Bank O2 Signal Low | Left Very Rich Offset | Right Bank Step Coil 3 On | TC ENG LvsR Hi Delta PSD | Right Eng O2 Hi CSD
14 | Right AUX O2 | 30015 | 14 | Right Bank Manual Override | Right Bank Exh Temp High | Left Getting Richer | Right Bank Step Coil 2 On | TC Eng Right Hi Temp PSD | Left Eng O2 Lo CSD
15 | Aux 1 0-5 Ratiometric | 30016 | 15 | Left Bank Manual Override | Right Bank Exh Temp Low | Left Auto Control is Active | Right Bank Step Coil 1 On | TC Eng Left Hi Temp PSD | Left Eng O2 Hi CSD
16 | Aux 2 0-5 Ratiometric | 30017
17 | Aux 3 0-5 Ratiometric | 30018
18 | Aux 4 0-5 Ratiometric | 30019
19 | Aux 1 Engineering Value | 30020
20 | Aux 2 Engineering Value | 30021
21 | Aux 3 Engineering Value | 30022
22 | Aux 4 Engineering Value | 30023
23 | Lookup Table A Result | 30024
24 | Lookup Table B Result | 30025
25 | Lookup Table C Result | 30026
26 | Lookup Table D Result | 30027
27 | Left O2 Dynamic Target | 30028
28 | Right O2 Dynamic Target | 30029
29 | Exhause Temp Delta | 30030
30 | Catalyst Temp Rise | 30031
31 | Calculator, signed sum | 30032
32 | Calculator, signed difference | 30033
33 | Calculator, absolute difference | 30034
34 | Calculator, x times y divided by 256 | 30035
35 | Calculator, signed filter 1 | 30036
36 | Calculator, signed filter 2 | 30037
37 | Control gain with dynamic offset | 30038
38 | Reserved | 30039
39 | Reserved | 30040
40 | Reserved | 30041
41 | Reserved | 30042
42 | Reserved | 30043
43 | Reserved | 30044
44 | Reserved | 30045
45 | Reserved | 30046
46 | Compliance SD Calc LT Timer | 30047
47 | Compliance ST GT Timer | 30048
48 | CSD Left/Right Telta Time | 30049
49 | CSD Cat In Temp Hi Time | 30050
50 | CSD Cat In Temp Lo Time | 30051
51 | CSD Cat Out Temp Hi Time | 30052
52 | CSD Cat Out Temp Lo Time | 30053
53 | CSD Cat Delta Temp Hi Time | 30054
54 | CSD Cat Delta Temp Lo Time | 30055
55 | CSD Left Bank O2 Hi Time | 30056
56 | CSD Left Bank O2 Lo Time | 30057
57 | CSD Right Bank O2 Hi Time | 30058
58 | CSD Right Bank O2 Lo Time | 30059
59 | CSD Cat In O2 Hi Time | 30060
60 | CSD Cat In O2 Lo Time | 30061
61 | CSD Cat Out O2 Hi Time | 30062
62 | CSD Cat Out O2 Lo Time | 30063
63 | Cause of NOT AUTO condition | 30084
64 | Autolog Left Eng Exh Temp | 30085
65 | Autolog Right Eng Exh Temp | 30086
66 | Autolog Left Eng O2 | 30087
67 | Autolog Right Eng O2 | 30088
68 | Autolog Left Stepper Position | 30089
69 | Autolog Right Stepper Position | 30090
70 | Autolog Left Aux TC | 30091
71 | Autolog Right Aux TC | 30092
72 | Autolog Aux1 O2 | 30093
73 | Autolog Aux2 O2 | 30094
74 | Autolog Analog 1 | 30095
75 | Autolog Analog 2 | 30096
76 | Autolog Analog 3 | 30097
77 | Autolog Analog 4 | 30098
78 | Aux TCR - Aux-TCL | 30099
79 | Aux 3 - Aux 4 | 30100
80 | CJT Comp | 30101
81 | A/D0 Filt | 30102
82 | A/D1 Filt Supply Voltage | 30103
83 | A/D2 Filt | 30104
84 | A/D3 CJT | 30105
85 | A/D4 O2 Right Legacy | 30106
86 | A/D5 O2 Left Legacy | 30107
87 | A/D6 TC Right Legacy | 30108
88 | A/D7 TC Left Legacy | 30109
89 | A/D8 TC Right Aux | 30110
90 | A/D9 TC Left Aux | 30111
91 | A/D O2 Right Aux | 30112
92 | A/D B O2 Left Aux | 30113
93 | A/D C Sensor 1 Aux | 30114
94 | A/D D Sensor 2 Aux | 30115
95 | A/D E Sensor 3 Aux | 30116
96 | A/D F Sensor 4 Aux | 30117
97 | Calc Filter *-1 | 30118
98 | Calc Filter 2 *-1 | 30119
99 | Warm Boot Counter | 30127
100 | Cold Boot Counter | 30128
101 | Communication Status Register | ***
102 | Bits 1 | 10001-10016
103 | Bits 2 | 10017-10032
104 | Bits 3 | 10033-10048
105 | Bits 4 | 10049-10064
106 | Bits 5 | 10065-10080
107 | Bits 6 | 10081-10096

## O2T
EPC100E:O.Data[n] | [6 empty] | Integers | Size: | 125
n | Value | EPC-100E Register | Min | Max | Default | Bits: | Output Bits | Data Type: | INT
0 | Left Bank O2 Target | 40001 | -32768 | 32767 | 800 | 0 | Reserved | Instance: | 101
1 | Right Bank O2 Target | 40002 | -32768 | 32767 | 800 | 1 | Reserved
2 | Left Bank Start Position | 40003 | -32768 | 32767 | 1000 | 2 | Reserved
3 | Right Bank Start Position | 40004 | -32768 | 32767 | 1000 | 3 | Reserved
4 | Control Gain Rate | 40005 | -32768 | 32767 | 20 | 4 | Output A
5 | Exh Temp Hi Alarm | 40006 | -32768 | 32767 | 1600 | 5 | Output B
6 | Exh Temp Lo Alarm | 40007 | -32768 | 32767 | 650 | 6 | Output C
7 | Exh O2 Hi Alarm Setpoint | 40008 | -32768 | 32767 | 1100 | 7 | Output D
8 | Exh O2 Lo Alarm Setpoint | 40009 | -32768 | 32767 | 10 | 8 | Reserved
9 | Exh O2 Ready Hi Setpoint | 40010 | -32768 | 32767 | 515 | 9 | Reserved
10 | Exh O2 Ready Lo Setpoint | 40011 | -32768 | 32767 | 485 | 10 | Reserved
11 | TC ENGOUT Hi PSD | 40012 | -32768 | 32767 | 1000 | 11 | Reserved
12 | TC ENG LvsR Hi PSD | 40013 | -32768 | 32767 | 100 | 12 | Reserved
13 | TC CAT In Hi PSD | 40014 | -32768 | 32767 | 1000 | 13 | Reserved
14 | TC CAT Out Hi PSD | 40015 | -32768 | 32767 | 1100 | 14 | Reserved
15 | TC Cat Delta Hi PSD | 40016 | -32768 | 32767 | 100 | 15 | Reserved
16 | PSD Cat Temp Delta I/O Lo | 40017 | -32768 | 32767 | -2000
17 | Calculator Input A Reg# | 40018 | -32768 | 32767 | 0
18 | Calculator Filter Value | 40019 | 0 | 255 | 0
19 | PSD Eng Out Temp Hi | 40020 | -32768 | 32767 | 600
20 | PSD Eng Out Temp L/R Delta Hi | 40021 | -32768 | 32767 | -6000
21 | CSD Eng Out Temp Delta L/R | 40022 | -32768 | 32767 | 2000
22 | CSD Cat In Temp Hi | 40023 | -32768 | 32767 | 2000
23 | CSD Cat In Temp Lo | 40024 | -32768 | 32767 | 2000
24 | CSD Cat Out Temp Hi | 40025 | -32768 | 32767 | 2000
25 | CSD Cat Out Temp Lo | 40026 | -32768 | 32767 | 2000
26 | CSD Cat Temp Delta I/O Hi | 40027 | -32768 | 32767 | 2000
27 | CSD Cat Temp Delta I/O Lo | 40028 | -32768 | 32767 | -2000
28 | CSD O2 Delay Time to Trip | 40029 | -32768 | 32767 | 600
29 | CSD O2 Start-up Disable Time | 40030 | -32768 | 32767 | -6000
30 | CSD Eng Out O2 Setpoint Hi | 40031 | -32768 | 32767 | 1200
31 | CSD Eng Out O2 Setpoint Lo | 40032 | -32768 | 32767 | 0
32 | CSD Cat In O2 Setpoint Hi | 40033 | -32768 | 32767 | 1200
33 | CSD Cat In O2 Setpoint Lo | 40034 | -32768 | 32767 | 0
34 | CSD Cat Out O2 Setpoint Hi | 40035 | -32768 | 32767 | 1200
35 | CSD Cat Out O2 Setpoint Lo | 40036 | -32768 | 32767 | 0
36 | Calculator Term A Reg# (A+B) | 40037 | -32768 | 32767 | 0
37 | Calculator Term B Reg# (A+B) | 40038 | -32768 | 32767 | 0
38 | Calculator Term A Reg# (A-B) | 40039 | -32768 | 32767 | 0
39 | Calculator Term B Reg# (A-B) | 40040 | -32768 | 32767 | 0
40 | Calculator Term A Reg# ¦A-B¦ | 40041 | -32768 | 32767 | 0
41 | Calculator Term B Reg# ¦A-B¦ | 40042 | -32768 | 32767 | 0
42 | Calculator Term A Reg# (AxB/256) | 40043 | -32768 | 32767 | 0
43 | Calculator Term B Reg# (AxB/256) | 40044 | -32768 | 32767 | 0
44 | Calcualtor Term A Reg# (Filtered) | 40045 | -32768 | 32767 | 0
45 | Calculator Filter Value | 40046 | 0 | 255 | 0
46 | Flex SPD Term B Reg# | 40047 | -32768 | 32767 | 0
47 | Flex PSD Term A Reg# | 40048 | -32768 | 32767 | 0
48 | Flex PSD Term C Reg# | 40049 | -32768 | 32767 | 0
49 | Flex CSD Term B Reg# | 40050 | -32768 | 32767 | 0
50 | Flex CSD Term A Reg# | 40051 | -32768 | 32767 | 0
51 | Flex CSD Term C Reg# | 40052 | -32768 | 32767 | 0
52 | Analog 1 Low Cal Counts | 40053 | 0 | 5000 | 500
53 | Analog 1 Cal Lo Units | 40054 | -32768 | 32767 | 500
54 | Analog 1 High Cal Volts | 40055 | 0 | 5000 | 4500
55 | Analog 1 Cal HighUnits | 40056 | -32768 | 32767 | 4500
56 | Analog 1 Abs Min Value | 40057 | -32768 | 32767 | 0
57 | Analog 1 Abs Max Value | 40058 | -32768 | 32767 | 5000
58 | Analog 2 Low Cal Volts | 40059 | 0 | 5000 | 500
59 | Analog 2 Cal Lo Units | 40060 | -32768 | 32767 | 500
60 | Analog 2 High Cal Volts | 40061 | 0 | 5000 | 4500
61 | Analog 2 Cal Hi Units | 40062 | -32768 | 32767 | 4500
62 | Analog 2 Abs Min Value | 40063 | -32768 | 32767 | 0
63 | Analog 2 Abs Max Value | 40064 | -32768 | 32767 | 5000
64 | Analog 3 Low Cal Volts | 40065 | 0 | 5000 | 500
65 | Analog 3 Cal Lo Units | 40066 | -32768 | 32767 | 500
66 | Analog 3 High Cal Volts | 40067 | 0 | 5000 | 4500
67 | Analog 3 Cal Hi Units | 40068 | -32768 | 32767 | 4500
68 | Analog 3 Abs Min Value | 40069 | -32768 | 32767 | 0
69 | Analog 3 Abs Max Value | 40070 | -32768 | 32767 | 5000
70 | Analog 4 Low Cal Volts | 40071 | 0 | 5000 | 500
71 | Analog 4 Cal Lo Units | 40072 | -32768 | 32767 | 500
72 | Analog 4 High Cal Volts | 40073 | 0 | 5000 | 4500
73 | Analog 4 Cal Hi Units | 40074 | -32768 | 32767 | 4500
74 | Analog 4 Abs Min Value | 40075 | -32768 | 32767 | 0
75 | Analog 4 Abs Max Value | 40076 | -32768 | 32767 | 5000
76 | Table A Source Reg# for X Value | 40077 | -32768 | 32767 | 0
77 | Table A Value X1 | 40078 | -32768 | 32767 | 0
78 | Table A Value Y1 | 40079 | -32768 | 32767 | 0
79 | Table A Value X2 | 40080 | -32768 | 32767 | 0
80 | Table A Value Y2 | 40081 | -32768 | 32767 | 0
81 | Table A Value X3 | 40082 | -32768 | 32767 | 0
82 | Table A Value Y3 | 40083 | -32768 | 32767 | 0
83 | Table A Value X4 | 40084 | -32768 | 32767 | 0
84 | Table A Value Y4 | 40085 | -32768 | 32767 | 0
85 | Table A Value X5 | 40086 | -32768 | 32767 | 0
86 | Table A Value Y5 | 40087 | -32768 | 32767 | 0
87 | Table B Source Reg# for X Value | 40088 | -32768 | 32767 | 0
88 | Table B Value X1 | 40089 | -32768 | 32767 | 0
89 | Table B Value Y1 | 40090 | -32768 | 32767 | 0
90 | Table B Value X2 | 40091 | -32768 | 32767 | 0
91 | Table B Value Y2 | 40092 | -32768 | 32767 | 0
92 | Table B Value X3 | 40093 | -32768 | 32767 | 0
93 | Table B Value Y3 | 40094 | -32768 | 32767 | 0
94 | Table B Value X4 | 40095 | -32768 | 32767 | 0
95 | Table B Value Y4 | 40096 | -32768 | 32767 | 0
96 | Table B Value X5 | 40097 | -32768 | 32767 | 0
97 | Table B Value Y5 | 40098 | -32768 | 32767 | 0
98 | Table C Source Reg# for X Value | 40099 | -32768 | 32767 | 0
99 | Table C Value X1 | 40100 | -32768 | 32767 | 0
100 | Table C Value Y1 | 40101 | -32768 | 32767 | 0
101 | Table C Value X2 | 40102 | -32768 | 32767 | 0
102 | Table C Value Y2 | 40103 | -32768 | 32767 | 0
103 | Table C Value X3 | 40104 | -32768 | 32767 | 0
104 | Table C Value Y3 | 40105 | -32768 | 32767 | 0
105 | Table C Value X5 | 40106 | -32768 | 32767 | 0
106 | Table C Value Y5 | 40107 | -32768 | 32767 | 0
107 | Table D Source Reg# for X Value | 40108 | -32768 | 32767 | 0
108 | Table D Value X1 | 40109 | -32768 | 32767 | 0
109 | Table D Value Y1 | 40110 | -32768 | 32767 | 0
110 | Table D Value X2 | 40111 | -32768 | 32767 | 0
111 | Table D Value Y2 | 40112 | -32768 | 32767 | 0
112 | Table D Value X3 | 40113 | -32768 | 32767 | 0
113 | Table D Value Y3 | 40114 | -32768 | 32767 | 0
114 | Table D Value X4 | 40115 | -32768 | 32767 | 0
115 | Table D Value Y4 | 40116 | -32768 | 32767 | 0
116 | Table D Value X5 | 40117 | -32768 | 32767 | 0
117 | Table D Value Y5 | 40118 | -32768 | 32767 | 0
118 | Spare | 40119 | -32768 | 32767 | 0
119 | Inhibit Auto Control Term A Reg# | 40121 | -32768 | 32767 | 0
120 | Inhibit < Value of A | 40122 | -32768 | 32767 | -32768
121 | Inhibit Auto Control Term B Reg# | 40123 | -32768 | 32767 | 0
122 | Inhibit > Value of B | 40124 | 0 | 32767 | 32767
123 | Output Bits | 40125 | -32768 | 32767 | 0
124 | Status Control | *** | -32767 | 32767 | 0