## T2O
VSM800:I.Data[n] |  |  |  | Integers |  |  |  |  | Size: | 38
n | Value | VSM-800 Register | Bits: | Diagnostic Bits | Bad Sensor Bits | Critical High Bits | High Bits | Armed Bits | Data Type: | INT
0 | Vibration Channel 1 | 30015 | 0 | Reserved | Bad Sensor 1 | Critical High 1 | Vibration High 1 | Channel Armed 1 | Instance: | 100
1 | Alarm Setpoint Channel 1 | 40044 | 1 | Reserved | Bad Sensor 2 | Critical High 2 | Vibration High 2 | Channel Armed 2
2 | Shutdown Setpoint Channel 1 | 40045 | 2 | SW1 Active | Bad Sensor 3 | Critical High 3 | Vibration High 3 | Channel Armed 3
3 | Bad Sensor Setpoint Channel 1 | 40046 | 3 | SW2 Active | Bad Sensor 4 | Critical High 4 | Vibration High 4 | Channel Armed 4
4 | Vibration Channel 2 | 30016 | 4 | Reserved | Bad Sensor 5 | Critical High 5 | Vibration High 5 | Channel Armed 5
5 | Alarm Setpoint Channel 2 | 40064 | 5 | Reserved | Bad Sensor 6 | Critical High 6 | Vibration High 6 | Channel Armed 6
6 | Shutdown Setpoint Channel 2 | 40065 | 6 | Reserved | Bad Sensor 7 | Critical High 7 | Vibration High 7 | Channel Armed 7
7 | Bad Sensor Setpoint Channel 2 | 40066 | 7 | Reserved | Bad Sensor 8 | Critical High 8 | Vibration High 8 | Channel Armed 8
8 | Vibration Channel 3 | 30017 | 8 | CAL R/W | Reserved | Reserved | Reserved | Reserved
9 | Alarm Setpoint Channel 3 | 40084 | 9 | Watchdog | Reserved | Reserved | Reserved | Reserved
10 | Shutdown Setpoint Channel 3 | 40085 | 10 | Reset | Reserved | Reserved | Reserved | Reserved
11 | Bad Sensor Setpoint Channel 3 | 40086 | 11 | Reserved | Reserved | Reserved | Reserved | Reserved
12 | Vibration Channel 4 | 30018 | 12 | Startup Locked Out | Reserved | Reserved | Reserved | Reserved
13 | Alarm Setpoint Channel 4 | 40104 | 13 | Alarm | Reserved | Reserved | Reserved | Reserved
14 | Shutdown Setpoint Channel 4 | 40105 | 14 | Reserved | Reserved | Reserved | Reserved | Reserved
15 | Bad Sensor Setpoint Channel 4 | 40106 | 15 | Reserved | Reserved | Reserved | Reserved | Reserved
16 | Vibration Channel 5 | 30019
17 | Alarm Setpoint Channel 5 | 40124
18 | Shutdown Setpoint Channel 5 | 40125
19 | Bad Sensor Setpoint Channel 5 | 40126
20 | Vibration Channel 6 | 30020
21 | Alarm Setpoint Channel 6 | 40144
22 | Shutdown Setpoint Channel 6 | 40145
23 | Bad Sensor Setpoint Channel 6 | 40146
24 | Vibration Channel 7 | 30021
25 | Alarm Setpoint Channel 7 | 40164
26 | Shutdown Setpoint Channel 7 | 40165
27 | Bad Sensor Setpoint Channel 7 | 40166
28 | Vibration Channel 8 | 30022
29 | Alarm Setpoint Channel 8 | 40184
30 | Shutdown Setpoint Channel 8 | 40185
31 | Bad Sensor Setpoint Channel 8 | 40186
32 | Diagnostic Bits | 10001-10016
33 | Bad Sensor Bits | 10017-10032
34 | Critical High Bits | 10033-10048
35 | High Bits | 10049-10064
36 | Armed Bits | 10065-10080
37 | Communication Status | ***

## O2T
VSM800:O.Data[n] | [5 empty] | Size: | 1
n | Value | VSM-800 Register | Min | Max | Default | Data Type: | INT
0 | Status Control | *** | -32767 | 32767 | 0 | Instance: | 101

## log (70h)
Attribute | ID | Tag | Data Type | Access | Minimum | Maximum | Instance ID Register | [31 empty] | Parameter Range: | 1-32
[7 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | Parameter Group(s): | 1-32
Event Log Entry | 1 | label | INT | RO |  |  | 30030 | 30031 | 30032 | 30033 | 30034 | 30035 | 30036 | 30037 | 30038 | 30039 | 30040 | 30041 | 30042 | 30043 | 30044 | 30045 | 30046 | 30047 | 30048 | 30049 | 30050 | 30051 | 30052 | 30053 | 30054 | 30055 | 30056 | 30057 | 30058 | 30059 | 30060 | 30061 | Group: | 1
[39 empty] | Label Service Supported: | Yes
[39 empty] | Key Command Service Supported: | Yes
[39 empty] | Number of Instances: | 32
[39 empty] | Number of Attributes: | 1
[39 empty] | Object Tag: | log
[39 empty] | Object ID: | 106
[39 empty] | Revision: | 2