## T2O
VSMPlus:I.Data[n] |  |  |  | Integers |  |  |  |  | Size: | 14
n | Value | VSM Register | Bits: | Diagnostic Bits | Bad Sensor Bits | Critical High Bits | High Bits | Armed Bits | Data Type: | INT
0 | Vibration Channel 1 | 30015 | 0 | Reserved | Bad Sensor 1 | Critical High 1 | Vibration High 1 | Channel Armed 1 | Instance: | 100
1 | Vibration Channel 2 | 30016 | 1 | Reserved | Bad Sensor 2 | Critical High 2 | Vibration High 2 | Channel Armed 2
2 | Vibration Channel 3 | 30017 | 2 | SW1 Active | Bad Sensor 3 | Critical High 3 | Vibration High 3 | Channel Armed 3
3 | Vibration Channel 4 | 30018 | 3 | SW2 Active | Bad Sensor 4 | Critical High 4 | Vibration High 4 | Channel Armed 4
4 | Vibration Channel 5 | 30019 | 4 | Reserved | Bad Sensor 5 | Critical High 5 | Vibration High 5 | Channel Armed 5
5 | Vibration Channel 6 | 30020 | 5 | Reserved | Bad Sensor 6 | Critical High 6 | Vibration High 6 | Channel Armed 6
6 | Vibration Channel 7 | 30021 | 6 | Reserved | Bad Sensor 7 | Critical High 7 | Vibration High 7 | Channel Armed 7
7 | Vibration Channel 8 | 30022 | 7 | Reserved | Bad Sensor 8 | Critical High 8 | Vibration High 8 | Channel Armed 8
8 | Supply Voltage | 30010 | 8 | CAL R/W | Reserved | Reserved | Reserved | Reserved
9 | Diagnostic Bits | 10001 | 9 | Watchdog | Reserved | Reserved | Reserved | Reserved
10 | Bad Sensor Bits | 10017 | 10 | Reset | Reserved | Reserved | Reserved | Reserved
11 | Critical High Bits | 10033 | 11 | Reserved | Reserved | Reserved | Reserved | Reserved
12 | High Bits | 10049 | 12 | Startup Locked Out | Reserved | Reserved | Reserved | Reserved
13 | Armed Bits | 10065 | 13 | Alarm | Reserved | Reserved | Reserved | Reserved
|  |  | 14 | Reserved | Reserved | Reserved | Reserved | Reserved
|  |  | 15 | Reserved | Reserved | Reserved | Reserved | Reserved

## O2T
VSMPlus:O.Data[n] | [6 empty] | Integers | Size: | 52
n | Value | VSM Register | Min | Max | Default | Bits: | Control Bits | Data Type: | INT
0 | Gain 1 | 40041 | 0 | 63 | 14 | 0 | Reserved | Instance: | 101
1 | Gain 2 | 40061 | 0 | 63 | 14 | 1 | Reserved
2 | Gain 3 | 40081 | 0 | 63 | 14 | 2 | Reserved
3 | Gain 4 | 40101 | 0 | 63 | 14 | 3 | Reserved
4 | Gain 5 | 40121 | 0 | 63 | 14 | 4 | Reserved
5 | Gain 6 | 40141 | 0 | 63 | 14 | 5 | Switch 1 Enabled
6 | Gain 7 | 40161 | 0 | 63 | 14 | 6 | Switch 1 State
7 | Gain 8 | 40181 | 0 | 63 | 14 | 7 | Switch 1 Latching
8 | Lag Filter | 40013 | 1 | 255 | 240 | 8 | Bad Sensor Switch Select
9 | Number of Channels | 40014 | 1 | 8 | 8 | 9 | Switch 2 Enabled
10 | Alarm Setpoint 1 | 40044 | 0 | 999 | 700 | 10 | Switch 2 State
11 | Shutdown Setpoint 1 | 40045 | 0 | 999 | 800 | 11 | Switch 2 Latching
12 | Bad Sensor Setpoint 1 | 40046 | 0 | 999 | 0 | 12 | Reserved
13 | Start Delay 1 | 40056 | 0 | 999 | 60 | 13 | Reserved
14 | Trip Delay 1 | 40057 | 0 | 15 | 3 | 14 | Reserved
15 | Alarm Setpoint 2 | 40064 | 0 | 999 | 700 | 15 | Startup Lockout
16 | Shutdown Setpoint 2 | 40065 | 0 | 999 | 800
17 | Bad Sensor Setpoint 2 | 40066 | 0 | 999 | 0
18 | Start Delay 2 | 40076 | 0 | 999 | 60
19 | Trip Delay 2 | 40077 | 0 | 15 | 3
20 | Alarm Setpoint 3 | 40084 | 0 | 999 | 700
21 | Shutdown Setpoint 3 | 40085 | 0 | 999 | 800
22 | Bad Sensor Setpoint 3 | 40086 | 0 | 999 | 0
23 | Start Delay 3 | 40096 | 0 | 999 | 60
24 | Trip Delay 3 | 40097 | 0 | 15 | 3
25 | Alarm Setpoint 4 | 40104 | 0 | 999 | 700
26 | Shutdown Setpoint 4 | 40105 | 0 | 999 | 800
27 | Bad Sensor Setpoint 4 | 40106 | 0 | 999 | 0
28 | Start Delay 4 | 40116 | 0 | 999 | 60
29 | Trip Delay 4 | 40117 | 0 | 15 | 3
30 | Alarm Setpoint 5 | 40124 | 0 | 999 | 700
31 | Shutdown Setpoint 5 | 40125 | 0 | 999 | 800
32 | Bad Sensor Setpoint 5 | 40126 | 0 | 999 | 0
33 | Start Delay 5 | 40136 | 0 | 999 | 60
34 | Trip Delay 5 | 40137 | 0 | 15 | 3
35 | Alarm Setpoint 6 | 40144 | 0 | 999 | 700
36 | Shutdown Setpoint 6 | 40145 | 0 | 999 | 800
37 | Bad Sensor Setpoint 6 | 40146 | 0 | 999 | 0
38 | Start Delay 6 | 40156 | 0 | 999 | 60
39 | Trip Delay 6 | 40157 | 0 | 15 | 3
40 | Alarm Setpoint 7 | 40164 | 0 | 999 | 700
41 | Shutdown Setpoint 7 | 40165 | 0 | 999 | 800
42 | Bad Sensor Setpoint 7 | 40166 | 0 | 999 | 0
43 | Start Delay 7 | 40176 | 0 | 999 | 60
44 | Trip Delay 7 | 40177 | 0 | 15 | 3
45 | Alarm Setpoint 8 | 40184 | 0 | 999 | 700
46 | Shutdown Setpoint 8 | 40185 | 0 | 999 | 800
47 | Bad Sensor Setpoint 8 | 40186 | 0 | 999 | 0
48 | Start Delay 8 | 40196 | 0 | 999 | 60
49 | Trip Delay 8 | 40197 | 0 | 15 | 3
50 | Switch Hysteresis Time | 40016 | 0 | 15 | 5
51 | Control Bits | 00001

## sensor (68h)
Attribute | ID | Tag | Data Type | Access | Minimum | Maximum | Instance ID Register | [7 empty] | Parameter Range: | 1-144
[7 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Parameter Group(s): | 1-8
Channel Label | 1 | label | STRING,DINT,SINT[82] | RW | 2 | 12 | 40050-40055 | 40070-40075 | 40090-40095 | 40110-40115 | 40130-40135 | 40150-40155 | 40170-40175 | 40190-40195 | Group: | 1
Prescale | 2 | prescale | INT | RW | 0 | 8 | 40040 | 40060 | 40080 | 40100 | 40120 | 40140 | 40160 | 40180 | Label Service Supported: | Yes
Gain | 3 | gain | INT | RW | 0 | 63 | 40041 | 40061 | 40081 | 40101 | 40121 | 40141 | 40161 | 40181 | Key Command Service Supported: | No
Bandpass | 4 | bandpass | INT | RW | 0 | 63 | 40042 | 40062 | 40082 | 40102 | 40122 | 40142 | 40162 | 40182 | Number of Instances: | 8
Time Constant | 5 | time_const | INT | RW | 0 | 31 | 40043 | 40063 | 40083 | 40103 | 40123 | 40143 | 40163 | 40183 | Number of Attributes: | 18
Alarm Setpoint | 6 | alm_sp | INT | RW | 0 | 999 | 40044 | 40064 | 40084 | 40104 | 40124 | 40144 | 40164 | 40184 | Object Tag: | sensor
Shutdown Setpoint | 7 | sd_sp | INT | RW | 0 | 999 | 40045 | 40065 | 40085 | 40105 | 40125 | 40145 | 40165 | 40185 | Object ID: | 104
Bad Sensor Setpoint | 8 | bad_snsr_sp | INT | RW | 0 | 999 | 40046 | 40066 | 40086 | 40106 | 40126 | 40146 | 40166 | 40186
Offset | 9 | offset | INT | RW | 0 | 500 | 40047 | 40067 | 40087 | 40107 | 40127 | 40147 | 40167 | 40187
Scalar | 10 | scalar | INT | RW | 0 | 9999 | 40048 | 40068 | 40088 | 40108 | 40128 | 40148 | 40168 | 40188
Label Type | 11 | label_type | INT | RW | 0 | 48 | 40049 | 40069 | 40089 | 40109 | 40129 | 40149 | 40169 | 40189
Start Delay | 12 | strt_dly | INT | RW | 0 | 999 | 40056 | 40076 | 40096 | 40116 | 40136 | 40156 | 40176 | 40196
Trip Timer | 13 | trip_tmr | INT | RW | 0 | 15 | 40057 | 40077 | 40097 | 40117 | 40137 | 40157 | 40177 | 40197
Vibration Level | 14 | vibration | INT | RO | 0 | 1024 | 30047 | 30048 | 30049 | 30050 | 30051 | 30052 | 30053 | 30054
Sensor Bad | 15 | sensor_stat | SINT | RO | 0 | 1 | 10017 | 10018 | 10019 | 10020 | 10021 | 10022 | 10023 | 10024
Switch 1 Tripped | 16 | sw1sp_trip | SINT | RO | 0 | 1 | 10049 | 10050 | 10051 | 10052 | 10053 | 10054 | 10055 | 10056
Switch 2 Tripped | 17 | sw2sp_trip | SINT | RO | 0 | 1 | 10033 | 10034 | 10035 | 10036 | 10037 | 10038 | 10039 | 10040
Channel Armed | 18 | armed | SINT | RO | 0 | 1 | 10065 | 10066 | 10067 | 10068 | 10069 | 10070 | 10071 | 10072

## vsm (69h)
Attribute | ID | Tag | Data Type | Access | Minimum | Maximum | Instance ID Register | Parameter Range: | 145-176
[7 empty] | 1 | Parameter Group(s): | 9
Lag Filter | 1 | lag_filter | INT | RW | 1 | 255 | 40013 | Group: | -n/a-
Number of Channels | 2 | no_chans | INT | RW | 1 | 8 | 40014 | Label Service Supported: | Yes
Window Length | 3 | window_len | INT | RW | 1 | 1500 | 40015 | Key Command Service Supported: | Yes
Switch 1 Hysteresis Time | 4 | sw1_hyst | INT | RW | 0 | 15 | 40016 | Number of Instances: | 1
Modulation Frequency | 5 | mod_freq | INT | RW | 0 | 65535 | 40017 | Number of Attributes: | 32
Common Offset Channels 1-4 | 6 | cmn_ofst_14 | INT | RW | 0 | 500 | 40018 | Object Tag: | vsm
Common Offset Channels 5-8 | 7 | cmn_ofst_58 | INT | RW | 0 | 500 | 40019 | Object ID: | 105
Filter Step | 8 | filt_step | INT | RW | 0 | 1024 | 40020
Filter Gain | 9 | filt_gain | INT | RW | 0 | 255 | 40021
Tens Only Mode | 10 | tens_only | SINT | RW | 0 | 1 | 00002
Switch 1 Enabled | 11 | sw1_en | SINT | RW | 0 | 1 | 00006
Switch 1 Latching | 12 | sw1_state | SINT | RW | 0 | 1 | 00007
Switch 1 Shelf/Failsafe | 13 | sw1_type | SINT | RW | 0 | 1 | 00008
Bad Sensor to Switch 1 | 14 | bad_snsr_sw | SINT | RW | 0 | 1 | 00009
Switch 2 Enabled | 15 | sw2_en | SINT | RW | 0 | 1 | 00010
Switch 2 Latching | 16 | sw2_state | SINT | RW | 0 | 1 | 00011
Switch 2 Shelf/Failsafe | 17 | sw2_type | SINT | RW | 0 | 1 | 00012
Reset | 18 | reset | SINT | RW | 0 | 1 | 00015
Control Lockout | 19 | lockout | SINT | RW | 0 | 1 | 00016
Switch 1 Active | 20 | sw1_active | SINT | RO | 0 | 1 | 10003
Switch 2 Active | 21 | sw2_active | SINT | RO | 0 | 1 | 10004
Factory Calibration Writable | 22 | cal_rw | SINT | RO | 0 | 1 | 10009
Watchdog Fault | 23 | watchdog | SINT | RO | 0 | 1 | 10010
Controls Reset | 24 | reset | SINT | RO | 0 | 1 | 10011
Controls Locked Out Externally | 25 | locked_out | SINT | RO | 0 | 1 | 10013
Alarm | 26 | alarm | SINT | RO | 0 | 1 | 10014
Hardware Model | 27 | hw_model | INT | RO | 4 | 8 | 30009
Supply Voltage | 28 | voltage | INT | RO | 0 | 3600 | 30010
Application CPU Utilization | 29 | cpu_usage | INT | RO | 0 | 100 | 30014
Device Identity | 30 | identity | ARRAY2_30,DINT,SINT[15] | RO |  |  | FN17 (5-20)
Device Status | 31 | status | ARRAY2_31, DINT,SINT[1] | RO |  |  | FN17 (2)
Device Version | 32 | version | ARRAY2_32,DINT,SINT[2] | RO |  |  | FN17 (3-4)

## log (70h)
Attribute | ID | Tag | Data Type | Access | Minimum | Maximum | Instance ID Register | [31 empty] | Parameter Range: | 177-208
[7 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | Parameter Group(s): | 10-42
Event Log Entry | 1 | label | INT | RO |  |  | 30030 | 30031 | 30032 | 30033 | 30034 | 30035 | 30036 | 30037 | 30038 | 30039 | 30040 | 30041 | 30042 | 30043 | 30044 | 30045 | 30046 | 30047 | 30048 | 30049 | 30050 | 30051 | 30052 | 30053 | 30054 | 30055 | 30056 | 30057 | 30058 | 30059 | 30060 | 30061 | Group: | 2
[39 empty] | Label Service Supported: | Yes
[39 empty] | Key Command Service Supported: | No
[39 empty] | Number of Instances: | 32
[39 empty] | Number of Attributes: | 1
[39 empty] | Object Tag: | log
[39 empty] | Object ID: | 106